## Sheet1
Drawing | Question | Response
C0.1 | Please clarify if the structure demolition, foundation demolition, site demolition and water/sewer lines demolition is included with the GC scope of work. | Refer to sheet C0.1 for the remaining demolition scope that is to be included. Anything noted as "part of separate demolition permit" is not in this scope, demolition of the structure is not in this scope.
| The RFP includes an alternate request for LEED certification. What level of certification is required for the alternate? | LEED Certified. Owner's LEED consultant will perform the LEED certification. General contractor to provide the requested materials and information and join monthly LEED check-in calls.
| When presenting final costs, does the owner prefer site pricing to be separate or broken out per building? | Separate.
| Please confirm that the existing fencing will remain for use with construction site security. | Existing fence can remain for construction site security, but is to be removed by end of project.
| Will new fences need to be installed? If so, please provide details. | Permanent fencing is not in project scope. If any temporary fencing is needed for construction, please include in pricing.
C1.0 | Please provide the thickness and reinforcement requirements for the Trash Enclosure (item 12) and Raised Utility Island (item 22) slabs per sheets C1.0. | Refer to geotech
S502 | Loading dock aprons thickness and reinforcement requirements are not included on the plans (S502). Please confirm that all loading dock aprons are to be 7-inch thick and non-reinforced concrete. | See geotech report and heavy concrete pavement sections called out on civil plans.
A101, S101A | The Keynote Legend (03/019) on sheet A101 calls out Ashford Formula (or approved equal) for the slab sealant. However on sheets S101A and S101B, it calls for Green Umbrella for the "Slab-on-Grade Curing Requirements." Please clarify which one is to be used. | Green Umbrella system is to be used. Green ice uses an additive that acts as sealant.
C3/G007 | FS0 wall type on sheet G007 indicates only rigid insulation at the concrete panels. Typically these wall types include metal stud furring with drywall one side. Please confirm FS0 wall types do not need metal stud furring. | FSO does not include any metal stud furring or drywall. That is placed where necessary and when at the time of Tenant Improvement. Not at shell. Insulation is to be placed directly to the wall.
| Are dock bumpers required for overhead doors that do not have dock levelers? | Yes, include dock bumpers at all loading dock locations.
| The 20'x20' overhead doors require a 42' clearance for the track to extend vertically. Please confirm that the joist and deck elevations are below the 42' clearance, so these tracks will need to be angled horizontally as it approaches joists and deck. If this is not acceptable, is a 14'x16' door acceptable? | Track goes up vertical, does a bend, then goes up along the joists.
C1.0 | Sheet C1.0 shows the locations for the monument sign footings however there are no details. Please provide requirements for footing thickness, dimensions, and reinforcement. | Monument sign footing details to be provided by monument sign vendor at a later date.
E001 | Will the monument signs require power? If so, please provide the conduit details. | No power to monument signs.
E101 | Sheets E101 do not include interior lighting for either warehouse. Please clarify what interior lighting is needed for each warehouse. | Warehouse high-bay lighting to be under separate spec TI scope.
| Please provide specifications for dock equipment and overhead doors. | Approved dock equipment is listed in hardware schedule.
| Is AMARR an approved supplier for the overhead doors? | yes
| Is AMARR commercial white acceptable in lieu of Kynar White? Are other white options acceptable? | yes
| Please confirm that 20x20 overhead doors have a full view glass section at the top. If so, please provide selection of glass that is needed for the full view section. | Sill of window to be placed between 8'-0" and 10'-0"
| It says 30,000 cycle springs on the dock and the bay doors, but we can only get 25,000 or 50,000, there’s no 30k option. Please verify whether they want 25 or 50. | Please provide a 30k minimum cycle. Please provide your bid with the lowest cycle you can with that min.Please state the cycles that are in bid.
| The hardware groups specify chain hoists on the dock doors, but not on the 20 x 20 doors. Typically, this is opposite. It’s uncommon for dock doors to have chain hoists. They are usually just manual. With larger doors, either having operators or chain hoists. Please verify. | All overhead doors including dock doors as well as 20x20 doors should have the chain pull for opening and closing doors.
| For the bumpers, do you want standard laminated bumpers or upgraded steel-faced bumpers? | Standard laminated
| On Sheet A531 Enlarged Canopy Plans (Details 6, 7) shows the canopies at 4’6” wide. The Canopy Sections 1 and 2 (Details 4, 5) show the canopies at 4’ wide. Please verify the width of the canopies. | The plan takes precedence and the canopies should be at 4'-6". Sections have been adjusted.
| We are seeking clarification regarding the glass specified as Viracon V28. Based on our review, the product appears similar to a Solarblue-type vision glass; however, the "V" designation is typically associated with a spandrel glass product in our system. Could you please confirm the exact glass type and intended application for this specification? | The glass should not be spandrel. This is to be a Solarblue type color Viricon glazing.
| Could you please confirm that the main roof deck is warped, requiring no crickets, but the canopies are fully tapered. | The main roof deck is warped and the canopies are fully tapered to get slopes.
| Please confirm the scale on A103. | Scales are accurate.
| The C-Sheets do not have any contour elevation on finish grade or natural grade, is it possible to get those? | See sheet C2.0, grading plans, civil CAD files
| Please provide the thickness and/or reinforcement of the concrete slabs for items 12 and 22 on Civil sheet C1.0: Trash Enclosure and Raised Utility Island. | Trash enclosure - can be the same thickness as the concrete pad that surrounds it. Utility island - the size is based on the gear specification and the depth is based on having a level surface for the length of the gear. the pad typically has a 3" larger house keeping pad around the gear and 3" above grade.
| Please confirm that all loading dock areas are 7" thick non-reinforced concrete | See geotech report and heavy concrete pavement sections called out on civil plans.
| On both buildings count of store front frame E on floor plan does not match count on Elevation page. Should the Floor plan or Elevation page prevail? | Window call outs on the floor plan have been updated.
| Do you want us to quote “dock seals” to go with the levelers or was that supposed to say “weather seals”? If no answer will assume weather seals. | Dock seal (not sure what is meant by "weather seal")
CAD | Are CAD civil drawings available to show current and new topo's. | Complete.
LP-101 | Landscaping maintenance period is not specified in plans or specs. Please specify maintenance period | GC to warranty landscaping. Owner to contract directly with landscaper for maintenance post- delivery of the project.
A101 | Keynote 05/001 states to paint columns yellow to 12'H. Will the rest of the way to bottom of deck be painted white or just primed from steel manufacture finished? | Primed
A521 | Roofing membrane is shown brought up and over top of parapet on sheet A502 where details on sheet A521 show various terminations. Please state where roofing membrane is supposed to terminate. | The TPO will go over the top of the parapet. That is a standard detail for areas where there is an overly tall parapet, and at areas where canopies have TPO running up the wall and how to terminate it.
A602 | A602 Calls out as spec to be Arcadia for Storefront Frames will Manco and Kawneer be approved equals? | This is acceptable
S001 | Soils report on structural drawings are called out as 02/13/2026 where Geotech report shared in files is dated 01/09/2026. Is the 01/09/2026 Geotech report the latest to be contracted from? | There is a site specific geotech report that was distributed on 2/13/2026
A602 | Will Trulite be an acceptable approved storefront equivalent to Arcadia. | This is acceptable
E001 | Per Keynote 6 on this sheet it is calling for RMP connection to nearest grid. Per conversations with RMP has this location been determined? | Refer to RMP System Impact Study. This is all the information we have at this time.
E201 | Keynote 1 indicates conduits that need to be run for future tenants. Are these to be run overhead or under slab? | Under slab
A601 | Building 1 shows (10) dock packages on floor plan and then in schedule calls out for (5). This will be an alternate but please confirm qty wanted for Bldg. 1. | Not exactly sure where the 10 is coming from. My floor plan shows 5 and matches the schedule.
Email | Please state which classification of LEED certification you are trying to obtain for this building. | LEED Certified. Owner's LEED consultant will perform the LEED certification. General contractor to provide the requested materials and information and join monthly LEED check-in calls.
NA | Will spec book be released for this project or just use in drawing specs? | No there will not be a spec book.
A301 | Battery and e-waste recycling area called out on sheet A101 keynote 10/005. Please state if this is a cabinet that needs to be furnished or painted area. Please advise. | There is nothing that needs to be done to this. This is a note for LEED purposes only and has no bearing or cost on construction.
Elec | Will heat tape be required at any of the roof drains or canopies. Currently not called out. | No heat tape will be needed. Canopy drainage goes inside the building then cow tongues out of the building.
LP-101 | Inorganic Mulch Specs on LP-101 call for a 12” depth of topsoil, while multiple details on page LP-501 call for 3” of topsoil mixed with 5” of existing soil and then 4” of topsoil on top of that which would be 7”. Please clarify this item. | We have started adjusting our plans to have 6" topsoil for under the mulch area where plants are located with 2" of topsoil mixed with the top 6" of soil and then 4" of topsoil placed on top of that.
LP-101 | Landscape spec 3.5, A, on LP-101 doesn’t recommend weed barrier fabric, please confirm weed barrier fabric is not to be used. | Please proceed with the weed barrier option noted in the landscape drawings.
LP-101, 501 | Landscape spec 2.1, F on LP-101 and detail A on LP-501 calls for a backfill mix of 80% native soil and 20% topsoil, while Inorganic Mulch Note on LP-101 calls for a 4:1 ratio of topsoil to compost. Please specify which backfill mix is to be used. | 80% native and 20% topsoil
IR-101 | Page IR-101 location overview calls for a 1.5” Mainline while page IR-103 calls for a 2” mainline. Please confirm we are to use 2” mainline. | 2" Mainline